## Sheet1
Failure Index | Start Time | End Time | Event | Category | Shutdown Type
1 | 2023-02-19 08:25:00 | 2023-02-19 10:16:00 | LGS#1 Trip by over frequency (Total blackout) | Electrical | Unplanned
2 | 2023-02-27 20:15:00 | 2023-02-27 20:35:00 | LGS#1 Trip by Line#1 and Line#2 Trip | Electrical | Unplanned
3 | 2023-03-10 22:53:00 | 2023-03-10 23:01:00 | LGS#1 Trip to standstill by over frequency (lightning strike) | Electrical | Unplanned
4 | 2023-04-24 03:57:00 | 2023-04-24 04:32:00 | LGS#1 trip by 186 TX hand reset lockout relay, Relay 186T / 18E relay energized | Electrical | Unplanned
5 | 2023-05-22 08:13:00 | 2023-05-22 08:32:00 | LGS#1 Trip by 86N energized, TGB Oil level low alarm trip | Mechanical | Unplanned
6 | 2023-07-31 10:49:00 | 2023-07-31 10:59:00 | LGS#1 Trip by under frequency | Electrical | Unplanned
7 | 2023-09-16 08:16:00 | 2023-09-16 09:36:00 | LGS#1 Trip by over frequency (Total blackout), 125 VDC power supply failed. | Electrical | Unplanned
8 | 2022-03-31 10:49:00 | 2022-03-31 11:18:00 | Furnace grid blackout, BUS Differential phase C trip | Electrical | Unplanned
9 | 2022-03-26 10:07:00 | 2022-03-26 13:50:00 | LGS#1 Trip by 86N energized due to Rotor shaft current stage-1 high trip | Mechanical | Unplanned
10 | 2022-03-26 16:17:00 | 2022-03-26 22:28:00 | LGS#1 suddenly trip by 86N due to Rotor shaft Current stage 2 high trip | Mechanical | Unplanned
11 | 2022-08-27 13:50:00 | 2022-08-27 14:51:00 | LGS#1 Trip due to A2-L2 CB suddenly trip opened | Electrical | Unplanned
12 | 2023-03-23 10:22:00 | 2023-03-23 12:34:00 | LGS#1 shut down for Hydran PPM reset | Instrument | Planned
13 | 2023-04-21 09:18:00 | 2023-04-21 11:27:00 | LGS#1 Shutdown for Replace Carbon Brush and clean up. | Mechanical | Planned
14 | 2023-05-29 11:34:00 | 2023-05-29 13:57:00 | LGS#1 Shutdown for Check & Repair Sensor Level oil TGB | Instrument | Planned
15 | 2023-07-13 11:27:00 | 2023-07-13 14:56:00 | LGS#1 Shutdown for Investigation TGB oil Level Low Trip Alarm. | Instrument | Planned
16 | 2023-07-20 07:45:00 | 2023-07-20 15:06:00 | LGS#1 Shutdown for HIRA | Mechanic, Electric, Instrument | Planned
17 | 2023-10-17 08:31:00 | 2023-10-17 16:21:00 | LGS#1 Shutdown For Check any Leakage on Servo W/G, Replace Carbon brush & General PM Check | Mechanic, Electric, Instrument | Planned
18 | 2023-11-21 06:33:00 | 2023-11-23 19:23:00 | LGS#1 Shutdown for Inspection by Indra Karya | Mechanic, Electric, Instrument | Planned
19 | 2022-01-06 09:23:00 | 2022-01-06 12:30:00 | LGS#1 Shutdown For Check & Repair Control Lead/Lag Governor#1-2 | Instrument | Planned
20 | 2022-01-14 09:59:00 | 2022-01-14 10:46:00 | LGS#1 Shutdown for Check Relay 489 & RTD | Instrument | Planned
21 | 2022-01-27 08:00:00 | 2022-01-27 14:32:00 | LGS#1 Shutdown for general PM check | Mechanic, Electric, Instrument | Planned
22 | 2022-02-04 15:57:00 | 2022-02-04 17:51:00 | LGS#1 Shutdown for check module modbus RTD multiline relay 489. | Electric, Instrument | Planned
23 | 2022-02-08 07:44:00 | 2022-02-11 20:52:00 | LGS#1 Shutdown for Check & Clean up Generator | Electric, Instrument | Planned
24 | 2022-03-22 06:00:00 | 2022-03-26 02:30:00 | LGS#1 Shutdown for MTX#1 Oil Conservator Bag replacement. | Electric | Planned
25 | 2022-04-05 09:23:00 | 2022-04-05 09:42:00 | LGS#1 Shutdown for replace plug servomotor LH for Wicket Gates | Mechanical | Planned
26 | 2022-05-23 05:30:00 | 2022-05-27 19:02:00 | LGS#1 S/Down for Clean Up Rotor-Stator & General PM Check | Mechanic, Electric, Instrument | Planned
27 | 2022-08-02 08:05:00 | 2022-08-02 19:31:00 | LGS#1 Shutdown For Replaced Card Module 64R, MTX Oil Level High Alarm & General PM Check. | Mechanic, Electric, Instrument | Planned
28 | 2022-09-15 07:11:00 | 2022-09-16 09:58:00 | LGS#1 Shutdown for Servomotor Check/Adjust & General PM Check | Mechanic, Electric, Instrument | Planned
29 | 2022-10-20 10:23:00 | 2022-10-20 13:30:00 | LGS#1 Shutdown for Check Kirk Key A1G1 CB & Check Synch Selector 143SS/A1G1 | Electrical | Planned
30 | 2022-12-07 10:07:00 | 2022-12-07 12:00:00 | LGS#1 Shutdown For Carbon Brush Replacement. | Electrical | Planned
31 | 2022-12-15 09:55:00 | 2022-12-15 17:10:00 | TLGS#1 Shutdown For PM Check Hira Turbine & Penstock | Mechanic, Electric, Instrument | Planned

## Sheet2
Start Time | End Time | Event | Activities | Related Component | Action/Cause | Interal/External | Shutdown Details | Startup Details | Supplied Grid after Action | Shutdown Type
2023-03-23 10:22:00 | 2023-03-23 12:34:00 | LGS#1 shut down for Hydran PPM reset | Instrument | Hydran PPM MTX | Alarm Reset | External | Shutdown via 4/CS | Started via 4/CS | Auxiliary Grid | Planned
2023-04-21 09:18:00 | 2023-04-21 11:27:00 | LGS#1 Shutdown for Replace Carbon Brush and clean up. | Instrument | Carbon Brush | Replacement | Internal | Shutdown | Started permissives | FCE Grid | Planned
2023-05-29 11:34:00 | 2023-05-29 13:57:00 | LGS#1 Shutdown for Check & Repair Sensor Level oil TGB | Instrument | TGB Oil Level Sensor | Installation Check | Internal | Shutdown | Started permissives | FCE Grid | Planned
2023-07-13 11:27:00 | 2023-07-13 14:56:00 | LGS#1 Shutdown for Investigation TGB oil Level Low Trip Alarm. | Instrument | TGB Oil Level Sensor | Alarm Check | Internal | Shutdown | Start from Local Panel | FCE Grid | Planned
2023-07-20 07:45:00 | 2023-07-20 15:06:00 | LGS#1 Shutdown for HIRA | Mechanic, Electric, Instrument | TGB Oil Level | Repairment | Internal | Shutdown | Start from Local Panel | FCE Grid | Planned
2023-10-17 08:31:00 | 2023-10-17 16:21:00 | LGS#1 Shutdown For Check any Leakage on Servo W/G, Replace Carbon brush & General PM Check | Mechanic, Electric, Instrument | Carbon Brush | Replacement | Internal | Shutdown | Start via 4/CS | FCE Grid | Planned
2023-11-21 06:33:00 | 2023-11-23 19:23:00 | LGS#1 Shutdown for Inspection by Indra Karya | Mechanic, Electric, Instrument | TGB Oil Level | Repairment | Internal | Shutdown | Start from Local Panel | FCE Grid | Planned
2022-01-06 09:23:00 | 2022-01-06 12:30:00 | LGS#1 Shutdown For Check & Repair Control Lead/Lag Governor#1-2 | Instrument | Governor | Repairment | Internal | Shutdown | Start to Speed No Load | FCE Grid | Planned
2022-01-14 09:59:00 | 2022-01-14 10:46:00 | LGS#1 Shutdown for Check Relay 489 & RTD | Instrument | Relay System | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-01-27 08:00:00 | 2022-01-27 14:32:00 | LGS#1 Shutdown for general PM check | Mechanic, Electric, Instrument | Carbon Brush | Replacement | Internal | Shutdown via HMI | Started via 4/CS | FCE Grid | Planned
2022-02-04 15:57:00 | 2022-02-04 17:51:00 | LGS#1 Shutdown for check module modbus RTD multiline relay 489. | Electric, Instrument | Relay System | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-02-08 07:44:00 | 2022-02-11 20:52:00 | LGS#1 Shutdown for Check & Clean up Generator | Electric, Instrument | Generator | Repairment | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-03-22 06:05:00 | 2022-03-26 02:30:00 | LGS#1 Shutdown for MTX#1 Oil Conservator Bag replacement. |  | MTX Bag | Replacement | External | Shutdown | Started via 4/CS | FCE Grid | Planned
2022-04-05 09:23:00 | 2022-04-05 09:42:00 | LGS#1 Shutdown for replace plug servomotor LH for Wicket Gates | Mechanical | Servo Motor Plug | Replacement | Internal | Shutdown | Started | FCE Grid | Planned
2022-05-23 05:30:00 | 2022-05-27 19:02:00 | LGS#1 S/Down for Clean Up Rotor-Stator & General PM Check | Mechanic, Electric, Instrument | Rotor | Repairment | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-08-02 08:06:00 | 2022-08-02 19:31:00 | LGS#1 Shutdown For Replaced Card Module 64R, MTX Oil Level High Alarm & General PM Check. | Mechanic, Electric, Instrument | MTX Oil | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-09-15 07:11:00 | 2022-09-16 09:58:00 | LGS#1 Shutdown for Servomotor Check/Adjust & General PM Check | Mechanic, Electric, Instrument | Carbon Brush | Replacement | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-10-20 10:23:00 | 2022-10-20 13:30:00 | LGS#1 Shutdown for Check Kirk Key A1G1 CB & Check Synch Selector 143SS/A1G1 | Electrical | A1G1 CB (Breaker) | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-12-07 10:07:00 | 2022-12-07 12:00:00 | LGS#1 Shutdown For Carbon Brush Replacement. | Electrical | Carbon Brush | Replacement | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-12-15 09:55:00 | 2022-12-15 17:10:00 | LGS#1 Shutdown For PM Check Hira Turbine & Penstock | Mechanic, Electric, Instrument | Turbine | Check | Internal | Shutdown via 5/CS and 4/CS | Started via 4/CS | FCE Grid | Planned
2021-01-18 08:03:00 | 2021-01-18 17:23:00 | LGS#1 shutdown for generator protection check, CW-101 Replace & Turbine Hira | Mechanic, Electric, Instrument | Generator Protection System | Check | Internal | Shutdown | Started | Auxiliary Grid | Planned
2021-01-19 08:20:00 | 2021-01-19 15:45:00 | LGS#1 shutdown for generator protection check cont. | Mechanic, Electric, Instrument | Generator Protection System | Check | Internal | Shutdown | Started | Auxiliary Grid | Planned
2021-02-04 09:20:00 | 2021-03-22 21:53:00 | LGS#1 shutdown for Replace Card LCB Cooling Water Flow , Replace Display UGB Cooling Water Flow and Replace MTX#1 | Mechanic, Electric, Instrument | Transofrmer | Replacement | External | Shutdown | Started via Local Panel | FCE Grid | Planned
2021-03-24 10:00:00 | 2021-03-24 16:20:00 | LGS#1 shut down for connect relay protection 187B | Electrical | Transofrmer | Check | External | Shutdown via 4/CS | Started via Local Panel | FCE Grid | Planned
2021-04-23 08:50:00 | 2021-04-23 14:38:00 | LGS#1 Shutdown for check & retorque bolt connection MTX | Mechanic, Electric, Instrument | Transofrmer | Repairment | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2021-05-20 07:53:00 | 2021-05-20 14:15:00 | LGS#1 Shutdown for check Vibration Sensor | Instrument | TGB | Instrument Check | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2021-06-14 00:15:00 | 2021-06-14 04:46:00 | LGS#1 shutdown for Replace relief valve CW-117 & RW 105 strainer drain unit#1 | Mechanic, Electric | Valve CW 117 | Replacement | Internal | Shutdown | Started via 4/CS | Auxiliary Grid | Planned
2021-08-27 09:45:00 | 2021-08-27 11:23:00 | LGS#1 Shutdown for Replace Module Processor T60 | Instrument | Module Processor T60 | Replacement | External | Shutdown to SNL |  | Auxiliary Grid | Planned
2021-09-23 05:58:00 | 2021-09-24 21:20:00 | LGS#1 Shutdown for SPM-D Synchronizer Check | Electrical, Instrument | Membrane Reducing Valve Cooling Water | Replacement | Internal | Shutdown via 4/CS |  | FCE Grid | Planned
2021-10-14 09:15:00 | 2021-10-15 00:18:00 | LGS#1 Shutdown for install SPM-A Synchronizer | Electrical, Instrument | SPM-A Synchronizer | Installation | External | Shutdown to SNL | Started via 4/CS | Auxiliary Grid | Planned
2021-10-26 09:46:00 | 2021-10-26 18:08:00 | LGS#1 Shutdown for Replacement A1G1 CB 150kV | Electrical, Instrument | A1T1 CB (Breaker) | Replacement | External | Shutdown via 4/CS | Started via 4/CS | Auxiliary Grid | Planned
2021-10-27 07:44:00 | 2021-10-30 00:33:00 | LGS#1 Shutdown for Replacement A1G1 CB 150kV | Electrical, Instrument | A1T1 CB (Breaker) | Check | External | Shutdown | Flying Started to SNL | FCE Grid | Planned
2020-01-15 16:02:00 | 2020-01-15 17:20:00 | LGS#1 Replace carbon brush | Electrical | Carbon Brush | Replacement | Internal | Shutdown via HMI | Started via HMI | FCE Grid | Planned
2020-03-13 06:00:00 | 2020-03-14 06:55:00 | LGS#1 Fox Oil and TGB Pot | Electrical | Generator | Check | Internal | Shutdown | Started via 4/CS | FCE Grid | Planned
2020-06-16 08:08:00 | 2020-06-16 19:14:00 | LGS#1 Replace carbon brush | Electrical | Carbon Brush | Replacement | Internal | Shutdown | Started via Local Panel | Auxiliary Grid | Planned
2020-07-28 08:09:00 | 2020-07-28 17:23:00 | LGS#1 Mech. OS 160% data & gen. PM Check | Mechanic, Electric, Instrument | Generator Excitatation System | Check | Internal | Shutdown | Started via HMI | FCE Grid | Planned
2020-10-01 08:29:00 | 2020-10-01 17:09:00 | LGS#1 Shut Down for Mechanical OS 160% Adjust & A1L2 CB check | Mechanic, Electric, Instrument | Generator | Check | Internal | Shutdown via 4/CS | Started via HMI | Auxiliary Grid | Planned
2020-10-05 08:43:00 | 2020-10-05 12:38:00 | LGS#1 shutdown for 125% Mechanical Over Speed | Mechanic, Instrument | Governor | Simulation | Internal |  |  |  | Planned
2020-10-22 09:16:00 | 2020-10-22 12:22:00 | LGS#1 shutdown for Blackout Simulation Test | Mechanic, Electric, Instrument | Generator System | Simulation | Internal | Shutdown via 4/CS | Started via HMI | FCE Grid | Planned
2020-11-12 08:09:00 | 2020-11-12 09:34:00 | LGS#1 shutdown for 135% Mechanical Over Speed Plate Adjustment & HIRA | Mechanic, Instrument | Governor | Simulation | Internal |  | Flying Started | Auxiliary Grid | Planned
2019-01-10 09:17:00 | 2019-01-10 09:28:00 | LGS#1 Shutdown for Load signal fail check & recondition | Instrument | Electrical System | Repairment | External | Shutdown to Standstill | Flying Started | FCE Grid | Planned
2019-04-26 09:44:00 | 2019-04-26 10:37:00 | LGS#1 Shut Down for PLC reset | Instrument | PLC System | Repairment | External | Shutdown to SNL | Started via HMI | FCE Grid | Planned
2019-09-10 07:20:00 | 2019-09-10 16:52:00 | LGS#1 Governor Press tank air make up adjusting & General PM Check | Mechanic, Electric, Instrument | Penstock Gate | Check | Internal | - | - | FCE Grid | Planned
2023-02-19 08:25:00 | 2023-02-19 10:16:00 | LGS#1 Trip by over frequency (Total blackout) | Electrical | A1L1 CB | Repairment | External | Trip by Over Frequency | Started via 4/CS | Auxiliary Grid | Unplanned
2023-02-27 20:15:00 | 2023-02-27 20:35:00 | LGS#1 Trip by Line#1 and Line#2 Trip | Electrical | A1L1 CB | Repairment | External | Trip by Over Frequency | Flying Started via 4/CS | Auxiliary Grid | Unplanned
2023-03-10 22:53:00 | 2023-03-10 23:01:00 | LGS#1 Trip to standstill | Electrical | A1L1CB | Repairment | External | Trip by Over Frequency | Flying Started | Auxiliary Grid | Unplanned
2023-04-24 03:57:00 | 2023-04-24 04:32:00 | LGS#1 trip by 186 TX hand reset lockout relay | Electrical | A1G1 CB | Repairment | External | Trip by 186 TX, 86 E Alarm | Flying Started | FCE Grid | Unplanned
2023-05-22 20:13:00 | 2023-05-22 20:32:00 | LGS#1 Trip by 86N energized | Mechanical | TGB Oil Level | Repairment | Internal | Trip by 86 N Alarm | Flying Started | FCE Grid | Unplanned
2023-07-31 10:49:00 | 2023-07-31 10:59:00 | LGS#1 Trip by under frequency | Electrical | FCE Grid | Repairment | External | Trip by Over Excitacy | - | FCE Grid | Unplanned
2023-09-16 08:16:00 | 2023-09-16 09:36:00 | LGS#1 Trip by over frequency (Total blackout) | Electrical | FCE Grid | Repairment | External | Trip by Over Frequency | - | FCE Grid | Unplanned
2023-10-04 22:01:00 | 2023-10-04 22:18:00 | Power Hydro to FCE’s grid Blackout. | Electrical | FCE Grid | Repairment | External | Trip | - | FCE Grid | Unplanned
2022-03-31 10:49:00 | 2022-03-31 11:18:00 | Furnace grid blackout | Electrical | FCE Grid | Repairment | External | Trip by Over Frequency | - | FCE Grid | Unplanned
2022-03-26 10:07:00 | 2022-03-26 13:50:00 | LGS#1 Trip by 86N energized | Mechanical | Rotor Shaft Current at Lower Generator | Repairment | Internal | Trip by 86N Alarm to Standstill | Start via 4/CS | FCE Grid | Unplanned
2022-03-26 16:17:00 | 2022-03-26 22:28:00 | LGS#1 suddenly trip by 86N due to Rotor shaft Current stage 2 high trip | Mechanical | Rotor Shaft Current at Lower Generator | Repairment | Internal | Trip by 86N Alarm to Standstill | Start | - | Unplanned
2022-08-27 13:50:00 | 2022-08-27 14:51:00 | Total blackout | Electrical | A2L2 CB | Repairment | External | Trip | Flying Started via 4/CS | Auxiliary Grid | Unplanned
2021-01-25 15:21:00 | 2021-01-25 16:10:00 | LGS#1 Trip by request from PLC Alarm | Instrument | A1G1 CB | Repairment | External | Trip by PLC Alarm | Started via 4/CS | Auxiliary Grid | Unplanned
2021-02-04 14:02:00 | 2021-02-04 23:59:59 | LGS#1 suddenly trip by 186T, 86E & 87GT differential trip. | Electrical | MTX | Repairment | External | Trip by 186 T, 86 E, 87 GT Alarm | Started via Local Panel | FCE Grid | Unplanned
2021-05-28 06:15:00 | 2021-05-30 0:58:00 | LGS#1 Trip by 86N energized | Mechanical | TGB Cooling Water | Repairment | Internal | Trip by 86N Alarm | Started via 4/CS | FCE Grid | Unplanned
2021-06-11 16:36:00 | 2021-06-11 16:57:00 | LGS#1 Trip to standstill | Electrical | A3G1 CB | Repairment | External | Trip by Under Frequency | Flying Started | FCE Grid | Unplanned
2021-11-13 11:47:00 | 2021-11-13 13:09:00 | LGS#1 Trip by under frequency | Electrical | FCE Grid | Repairment | External | Trip by Under Frequency | - | FCE Grid | Unplanned
2021-12-02 14:56:00 | 2021-12-02 18:00:00 | LGS#1 Trip to speed no load | Electrical | FCE Grid | Repairment | External | Trip to Speed No Load | - | FCE Grid | Unplanned
2021-12-14 19:34:00 | 2021-12-14 20:24:00 | LGS#1 Trip to standstill | Electrical | Line#1 | Thunder Strike | External | Trip by Over Frequency | Flying Started | FCE Grid | Unplanned
2020-02-14 16:38:00 | 2020-02-14 18:20:00 | LGS#1 Trip to standstill | Electrical | FCE Grid | Hydro Total Blackout | External | Trip to Standstill | - | Auxiliary Grid | Unplanned
2020-03-19 10:59:00 | 2020-03-19 11:11:00 | LGS#1 Trip by under frequency | Electrical | A3G1 CB | Breaker Trip | External | Trip by Under Frequency | Flying Start | FCE Grid | Unplanned
2020-05-25 16:58:00 | 2020-05-25 19:11:00 | LGS#1 Trip by under frequency | Electrical | A1G1 CB | Thunder Strike | External | Trip by Under Frequency | Flying Start | FCE Grid | Unplanned
2020-05-27 18:26:00 | 2020-05-28 01:21:00 | LGS#1 Trip to standstill | Electrical | A1G1 CB | Hydro to Grid Blackout | External | Trip by Over Speed | Started | FCE Grid | Unplanned
2020-09-15 22:47:00 | 2020-09-16 00:09:00 | Furnace grid blackout | Electrical | A1G1 CB | Breaker Trip | External | Trip | Flying Start | FCE Grid | Unplanned
2020-10-13 14:24:00 | 2020-10-14 02:33:00 | LGS#1 Trip to standstill | Electrical | A1G1 CB | Hydro Total Blackout | External | Trip by 86 E Alarm | Flying Start | FCE Grid | Unplanned
2020-12-24 18:59:00 | 2020-12-24 19:39:00 | Total blackout | Electrical | A1L1 CB | Hydro Total Blackout | External | Trip to Standstill | Started to SNL | Auxiliary Grid | Unplanned
2019-02-02 17:52:00 | 2019-02-02 18:16:00 | LGS#1 Trip by lockout relay 86E | Electrical | Fire Deluge System | Unknown Reason | Internal | Trip by 86 E. 186T Alarm | - | FCE Grid | Unplanned
2019-04-21 01:15:00 | 2019-04-21 01:25:00 | LGS#1 Trip by 86N normal shutdown | Mechanical | Governor Oil | Low Pressure | Internal | Trip by 86N Alarm | Flying Start | FCE Grid | Unplanned
2019-04-25 06:07:00 | 2019-04-25 11:27:00 | LGS#1 Trip by 86E energized | Mechanical | Governor Turbine | Alarm Trip | Internal | Trip by 86E Alarm | Start | FCE Grid | Unplanned
2019-04-26 07:14:00 | 2019-04-26 07:19:00 | LGS#1 Trip by 86E energized |  | A1G1 CB | Breaker Trip | External | Trip by 86E Alarm | Flying Start | FCE Grid | Unplanned
2019-04-27 07:51:00 | 2019-04-27 08:11:00 | LGS#1 Trip by 86E energized | Electrical | A1G1 CB | Breaker Trip | External | Trip by 86 E Alarm | Flying Start | FCE Grid | Unplanned
2019-04-28 04:23:00 | 2019-04-28 04:35:00 | LGS#1 Trip by relay 86E & 86T tripped | Electrical | A1G1 CB | Breaker Trip | External | Trip by 86E, 86T Alarm | Flying Start | FCE Grid | Unplanned
2019-04-28 23:30:00 | 2019-04-28 23:33:00 | LGS#1 Trip by relay 86E & 86T tripped | Electrical | A1G1 CB | Breaker Trip | External | Trip by 86E, 86T Alarm | Flying Start | FCE Grid | Unplanned
2019-05-23 09:44:00 | 2019-05-23 11:45:00 | Total blackout | Electrical | A3L3 CB | Total Blackout | External | Trip | Flying Start | FCE Grid | Unplanned
2019-06-29 00:51:00 | 2019-06-29 12:06:00 | LGS#1 Trip due to relay 186T transformer lock out relay tripped | Electrical | A1G1 CB | Thermal Plant Shorted | External | Trip by 186T Alarm | Started via 4/CS | FCE Grid | Unplanned
2019-10-16 05:57:00 | 2019-10-16 06:31:00 | Total blackout | Electrical | A1L2 CB | Trip | External | Trip | Flying Start | FCE Grid | Unplanned
2019-12-14 19:14:00 | 2019-12-14 22:32:00 | LGS#1 Trip to standstill due to PLC error. | Instrument | A1G1 CB | PLC Major Fault | External | Trip to Standstill | Started via HMI | FCE Grid | Unplanned
2019-12-25 23:52:00 | 2019-12-26 00:16:00 | LGS#1 trip to srandstill by electrical overSpeed | Electrical | A1G1 CB | Thunder Strike | External | Trip to Standstill | Flying Start | FCE Grid

## Sheet3
Start Time | End Time | Outage Duration | Shutdown Duration | Event | Problem | Activities | Related Component | Action/Cause | Interal/External | Shutdown Details | Startup Details | Supplied Grid after Action | Shutdown Type | Related Parameter | Note
2023-03-23 10:22:00 | 2023-03-23 12:34:00 | 132 |  | LGS#1 shut down for Hydran PPM reset |  | Instrument | Hydran PPM MTX | Alarm Reset | External | Shutdown via 4/CS | Started via 4/CS | Auxiliary Grid | Planned
2023-04-21 09:18:00 | 2023-04-21 11:27:00 | 129 |  | LGS#1 Shutdown for Replace Carbon Brush and clean up. |  | Instrument | Carbon Brush | Replacement | Internal | Shutdown | Started permissives | FCE Grid | Planned
2023-05-29 11:34:00 | 2023-05-29 13:57:00 | 143 |  | LGS#1 Shutdown for Check & Repair Sensor Level oil TGB |  | Instrument | TGB Oil Level Sensor | Installation Check | Internal | Shutdown | Started permissives | FCE Grid | Planned
2023-07-13 11:27:00 | 2023-07-13 14:56:00 | 209 |  | LGS#1 Shutdown for Investigation TGB oil Level Low Trip Alarm. |  | Instrument | TGB Oil Level Sensor | Alarm Check | Internal | Shutdown | Start from Local Panel | FCE Grid | Planned
2023-07-20 07:45:00 | 2023-07-20 15:06:00 | 441 |  | LGS#1 Shutdown for HIRA |  | Mechanic, Electric, Instrument | TGB Oil Level | Repairment | Internal | Shutdown | Start from Local Panel | FCE Grid | Planned
2023-10-17 08:31:00 | 2023-10-17 16:21:00 | 470 |  | LGS#1 Shutdown For Check any Leakage on Servo W/G, Replace Carbon brush & General PM Check |  | Mechanic, Electric, Instrument | Carbon Brush | Replacement | Internal | Shutdown | Start via 4/CS | FCE Grid | Planned
2023-11-21 06:33:00 | 2023-11-23 19:23:00 | 3650 |  | LGS#1 Shutdown for Inspection by Indra Karya |  | Mechanic, Electric, Instrument | TGB Oil Level | Repairment | Internal | Shutdown | Start from Local Panel | FCE Grid | Planned
2022-01-06 09:23:00 | 2022-01-06 12:30:00 | 187 |  | LGS#1 Shutdown For Check & Repair Control Lead/Lag Governor#1-2 |  | Instrument | Governor | Repairment | Internal | Shutdown | Start to Speed No Load | FCE Grid | Planned
2022-01-14 09:59:00 | 2022-01-14 10:46:00 | 47 |  | LGS#1 Shutdown for Check Relay 489 & RTD |  | Instrument | Relay System | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-01-27 08:00:00 | 2022-01-27 14:32:00 | 392 |  | LGS#1 Shutdown for general PM check |  | Mechanic, Electric, Instrument | Carbon Brush | Replacement | Internal | Shutdown via HMI | Started via 4/CS | FCE Grid | Planned
2022-02-04 15:57:00 | 2022-02-04 17:51:00 | 114 |  | LGS#1 Shutdown for check module modbus RTD multiline relay 489. |  | Electric, Instrument | Relay System | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-02-08 07:44:00 | 2022-02-11 20:52:00 | 5108 |  | LGS#1 Shutdown for Check & Clean up Generator |  | Electric, Instrument | Generator | Repairment | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-03-22 06:05:00 | 2022-03-26 02:30:00 | 5545 |  | LGS#1 Shutdown for MTX#1 Oil Conservator Bag replacement. |  |  | MTX Bag | Replacement | External | Shutdown | Started via 4/CS | FCE Grid | Planned
2022-04-05 09:23:00 | 2022-04-05 09:42:00 | 19 |  | LGS#1 Shutdown for replace plug servomotor LH for Wicket Gates |  | Mechanical | Servo Motor Plug | Replacement | Internal | Shutdown | Started | FCE Grid | Planned
2022-05-23 05:30:00 | 2022-05-27 19:02:00 | 6572 |  | LGS#1 S/Down for Clean Up Rotor-Stator & General PM Check |  | Mechanic, Electric, Instrument | Rotor | Repairment | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-08-02 08:06:00 | 2022-08-02 19:31:00 | 685 |  | LGS#1 Shutdown For Replaced Card Module 64R, MTX Oil Level High Alarm & General PM Check. |  | Mechanic, Electric, Instrument | MTX Oil | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-09-15 07:11:00 | 2022-09-16 09:58:00 | 1607 |  | LGS#1 Shutdown for Servomotor Check/Adjust & General PM Check |  | Mechanic, Electric, Instrument | Carbon Brush | Replacement | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-10-20 10:23:00 | 2022-10-20 13:30:00 | 187 |  | LGS#1 Shutdown for Check Kirk Key A1G1 CB & Check Synch Selector 143SS/A1G1 |  | Electrical | A1G1 CB (Breaker) | Check | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-12-07 10:07:00 | 2022-12-07 12:00:00 | 113 |  | LGS#1 Shutdown For Carbon Brush Replacement. |  | Electrical | Carbon Brush | Replacement | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2022-12-15 09:55:00 | 2022-12-15 17:10:00 | 435 |  | LGS#1 Shutdown For PM Check Hira Turbine & Penstock |  | Mechanic, Electric, Instrument | Turbine | Check | Internal | Shutdown via 5/CS and 4/CS | Started via 4/CS | FCE Grid | Planned
2021-01-18 08:03:00 | 2021-01-18 17:23:00 | 560 |  | LGS#1 shutdown for generator protection check, CW-101 Replace & Turbine Hira |  | Mechanic, Electric, Instrument | Generator Protection System | Check | Internal | Shutdown | Started | Auxiliary Grid | Planned
2021-01-19 08:20:00 | 2021-01-19 15:45:00 | 445 |  | LGS#1 shutdown for generator protection check cont. |  | Mechanic, Electric, Instrument | Generator Protection System | Check | Internal | Shutdown | Started | Auxiliary Grid | Planned
2021-02-04 09:20:00 | 2021-03-22 21:53:00 | 66993 |  | LGS#1 shutdown for Replace Card LCB Cooling Water Flow , Replace Display UGB Cooling Water Flow and Replace MTX#1 |  | Mechanic, Electric, Instrument | Transofrmer | Replacement | External | Shutdown | Started via Local Panel | FCE Grid | Planned
2021-03-24 10:00:00 | 2021-03-24 16:20:00 | 380 |  | LGS#1 shut down for connect relay protection 187B |  | Electrical | Transofrmer | Check | External | Shutdown via 4/CS | Started via Local Panel | FCE Grid | Planned
2021-04-23 08:50:00 | 2021-04-23 14:38:00 | 348 |  | LGS#1 Shutdown for check & retorque bolt connection MTX |  | Mechanic, Electric, Instrument | Transofrmer | Repairment | External | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2021-05-20 07:53:00 | 2021-05-20 14:15:00 | 382 |  | LGS#1 Shutdown for check Vibration Sensor |  | Instrument | TGB | Instrument Check | Internal | Shutdown via 4/CS | Started via 4/CS | FCE Grid | Planned
2021-06-14 00:15:00 | 2021-06-14 04:46:00 | 271 |  | LGS#1 shutdown for Replace relief valve CW-117 & RW 105 strainer drain unit#1 |  | Mechanic, Electric | Valve CW 117 | Replacement | Internal | Shutdown | Started via 4/CS | Auxiliary Grid | Planned
2021-08-27 09:45:00 | 2021-08-27 11:23:00 | 98 |  | LGS#1 Shutdown for Replace Module Processor T60 |  | Instrument | Module Processor T60 | Replacement | External | Shutdown to SNL |  | Auxiliary Grid | Planned
2021-09-23 05:58:00 | 2021-09-24 21:20:00 | 2362 |  | LGS#1 Shutdown for SPM-D Synchronizer Check |  | Electrical, Instrument | Membrane Reducing Valve Cooling Water | Replacement | Internal | Shutdown via 4/CS |  | FCE Grid | Planned
2021-10-14 09:15:00 | 2021-10-15 00:18:00 | 903 |  | LGS#1 Shutdown for install SPM-A Synchronizer |  | Electrical, Instrument | SPM-A Synchronizer | Installation | External | Shutdown to SNL | Started via 4/CS | Auxiliary Grid | Planned
2021-10-26 09:46:00 | 2021-10-26 18:08:00 | 502 |  | LGS#1 Shutdown for Replacement A1G1 CB 150kV |  | Electrical, Instrument | A1T1 CB (Breaker) | Replacement | External | Shutdown via 4/CS | Started via 4/CS | Auxiliary Grid | Planned
2021-10-27 07:44:00 | 2021-10-30 00:33:00 | 3889 |  | LGS#1 Shutdown for Replacement A1G1 CB 150kV |  | Electrical, Instrument | A1T1 CB (Breaker) | Check | External | Shutdown | Flying Started to SNL | FCE Grid | Planned
2020-01-15 16:02:00 | 2020-01-15 17:20:00 | 78 |  | LGS#1 Replace carbon brush |  | Electrical | Carbon Brush | Replacement | Internal | Shutdown via HMI | Started via HMI | FCE Grid | Planned
2020-03-13 06:00:00 | 2020-03-14 06:55:00 | 1495 |  | LGS#1 Fox Oil and TGB Pot |  | Electrical | Generator | Check | Internal | Shutdown | Started via 4/CS | FCE Grid | Planned
2020-06-16 08:08:00 | 2020-06-16 19:14:00 | 666 |  | LGS#1 Replace carbon brush |  | Electrical | Carbon Brush | Replacement | Internal | Shutdown | Started via Local Panel | Auxiliary Grid | Planned
2020-07-28 08:09:00 | 2020-07-28 17:23:00 | 554 |  | LGS#1 Mech. OS 160% data & gen. PM Check |  | Mechanic, Electric, Instrument | Generator Excitatation System | Check | Internal | Shutdown | Started via HMI | FCE Grid | Planned
2020-10-01 08:29:00 | 2020-10-01 17:09:00 | 520 |  | LGS#1 Shut Down for Mechanical OS 160% Adjust & A1L2 CB check |  | Mechanic, Electric, Instrument | Generator | Check | Internal | Shutdown via 4/CS | Started via HMI | Auxiliary Grid | Planned
2020-10-05 08:43:00 | 2020-10-05 12:38:00 | 235 |  | LGS#1 shutdown for 125% Mechanical Over Speed |  | Mechanic, Instrument | Governor | Simulation | Internal |  |  |  | Planned
2020-10-22 09:16:00 | 2020-10-22 12:22:00 | 186 |  | LGS#1 shutdown for Blackout Simulation Test |  | Mechanic, Electric, Instrument | Generator System | Simulation | Internal | Shutdown via 4/CS | Started via HMI | FCE Grid | Planned
2020-11-12 08:09:00 | 2020-11-12 09:34:00 | 85 |  | LGS#1 shutdown for 135% Mechanical Over Speed Plate Adjustment & HIRA |  | Mechanic, Instrument | Governor | Simulation | Internal |  | Flying Started | Auxiliary Grid | Planned
2019-01-10 09:17:00 | 2019-01-10 09:28:00 | 11 | 0 | LGS#1 Shutdown for Load signal fail check & recondition | Signal crimping cable was broke | Instrument | Electrical System | Repairment | External | Shutdown to Standstill | Flying Started | FCE Grid | Planned | Active Power, Reactive Power | Standstill condition categorized as Shutdown/Startup Process
2019-04-26 09:44:00 | 2019-04-26 10:37:00 | 53 |  | LGS#1 Shut Down for PLC reset |  | Instrument | PLC System | Repairment | External | Shutdown to SNL | Started via HMI | FCE Grid | Planned
2019-09-10 07:20:00 | 2019-09-10 16:52:00 | 572 |  | LGS#1 Governor Press tank air make up adjusting & General PM Check |  | Mechanic, Electric, Instrument | Penstock Gate | Check | Internal | - | - | FCE Grid | Planned
2023-02-19 08:25:00 | 2023-02-19 10:16:00 | 111 |  | LGS#1 Trip by over frequency (Total blackout) |  | Electrical | A1L1 CB | Repairment | External | Trip by Over Frequency | Started via 4/CS | Auxiliary Grid | Unplanned
2023-02-27 20:15:00 | 2023-02-27 20:35:00 | 20 |  | LGS#1 Trip by Line#1 and Line#2 Trip |  | Electrical | A1L1 CB | Repairment | External | Trip by Over Frequency | Flying Started via 4/CS | Auxiliary Grid | Unplanned
2023-03-10 22:53:00 | 2023-03-10 23:01:00 | 8 |  | LGS#1 Trip to standstill |  | Electrical | A1L1CB | Repairment | External | Trip by Over Frequency | Flying Started | Auxiliary Grid | Unplanned
2023-04-24 03:57:00 | 2023-04-24 04:32:00 | 35 |  | LGS#1 trip by 186 TX hand reset lockout relay |  | Electrical | A1G1 CB | Repairment | External | Trip by 186 TX, 86 E Alarm | Flying Started | FCE Grid | Unplanned
2023-05-22 20:13:00 | 2023-05-22 20:32:00 | 19 |  | LGS#1 Trip by 86N energized |  | Mechanical | TGB Oil Level | Repairment | Internal | Trip by 86 N Alarm | Flying Started | FCE Grid | Unplanned
2023-07-31 10:49:00 | 2023-07-31 10:59:00 | 10 |  | LGS#1 Trip by under frequency |  | Electrical | FCE Grid | Repairment | External | Trip by Over Excitacy | - | FCE Grid | Unplanned
2023-09-16 08:16:00 | 2023-09-16 09:36:00 | 80 |  | LGS#1 Trip by over frequency (Total blackout) |  | Electrical | FCE Grid | Repairment | External | Trip by Over Frequency | - | FCE Grid | Unplanned
2023-10-04 22:01:00 | 2023-10-04 22:18:00 | 17 |  | Power Hydro to FCE’s grid Blackout. |  | Electrical | FCE Grid | Repairment | External | Trip | - | FCE Grid | Unplanned
2022-03-31 10:49:00 | 2022-03-31 11:18:00 | 29 |  | Furnace grid blackout |  | Electrical | FCE Grid | Repairment | External | Trip by Over Frequency | - | FCE Grid | Unplanned
2022-03-26 10:07:00 | 2022-03-26 13:50:00 | 223 |  | LGS#1 Trip by 86N energized |  | Mechanical | Rotor Shaft Current at Lower Generator | Repairment | Internal | Trip by 86N Alarm to Standstill | Start via 4/CS | FCE Grid | Unplanned
2022-03-26 16:17:00 | 2022-03-26 22:28:00 | 371 |  | LGS#1 suddenly trip by 86N due to Rotor shaft Current stage 2 high trip |  | Mechanical | Rotor Shaft Current at Lower Generator | Repairment | Internal | Trip by 86N Alarm to Standstill | Start | - | Unplanned
2022-08-27 13:50:00 | 2022-08-27 14:51:00 | 61 |  | Total blackout |  | Electrical | A2L2 CB | Repairment | External | Trip | Flying Started via 4/CS | Auxiliary Grid | Unplanned
2021-01-25 15:21:00 | 2021-01-25 16:10:00 | 49 |  | LGS#1 Trip by request from PLC Alarm |  | Instrument | A1G1 CB | Repairment | External | Trip by PLC Alarm | Started via 4/CS | Auxiliary Grid | Unplanned
2021-02-04 14:02:00 | 2021-02-04 23:59:59 | 597.9833 |  | LGS#1 suddenly trip by 186T, 86E & 87GT differential trip. |  | Electrical | MTX | Repairment | External | Trip by 186 T, 86 E, 87 GT Alarm | Started via Local Panel | FCE Grid | Unplanned
2021-05-28 06:15:00 | 2021-05-30 0:58:00 | 2563 |  | LGS#1 Trip by 86N energized |  | Mechanical | TGB Cooling Water | Repairment | Internal | Trip by 86N Alarm | Started via 4/CS | FCE Grid | Unplanned
2021-06-11 16:36:00 | 2021-06-11 16:57:00 | 21 |  | LGS#1 Trip to standstill |  | Electrical | A3G1 CB | Repairment | External | Trip by Under Frequency | Flying Started | FCE Grid | Unplanned
2021-11-13 11:47:00 | 2021-11-13 13:09:00 | 82 |  | LGS#1 Trip by under frequency |  | Electrical | FCE Grid | Repairment | External | Trip by Under Frequency | - | FCE Grid | Unplanned
2021-12-02 14:56:00 | 2021-12-02 18:00:00 | 184 |  | LGS#1 Trip to speed no load |  | Electrical | FCE Grid | Repairment | External | Trip to Speed No Load | - | FCE Grid | Unplanned
2021-12-14 19:34:00 | 2021-12-14 20:24:00 | 50 |  | LGS#1 Trip to standstill |  | Electrical | Line#1 | Thunder Strike | External | Trip by Over Frequency | Flying Started | FCE Grid | Unplanned
2020-02-14 16:38:00 | 2020-02-14 18:20:00 | 102 |  | LGS#1 Trip to standstill |  | Electrical | FCE Grid | Hydro Total Blackout | External | Trip to Standstill | - | Auxiliary Grid | Unplanned
2020-03-19 10:59:00 | 2020-03-19 11:11:00 | 12 |  | LGS#1 Trip by under frequency |  | Electrical | A3G1 CB | Breaker Trip | External | Trip by Under Frequency | Flying Start | FCE Grid | Unplanned
2020-05-25 16:58:00 | 2020-05-25 19:11:00 | 133 |  | LGS#1 Trip by under frequency |  | Electrical | A1G1 CB | Thunder Strike | External | Trip by Under Frequency | Flying Start | FCE Grid | Unplanned
2020-05-27 18:26:00 | 2020-05-28 01:21:00 | 415 |  | LGS#1 Trip to standstill |  | Electrical | A1G1 CB | Hydro to Grid Blackout | External | Trip by Over Speed | Started | FCE Grid | Unplanned
2020-09-15 22:47:00 | 2020-09-16 00:09:00 | 82 |  | Furnace grid blackout |  | Electrical | A1G1 CB | Breaker Trip | External | Trip | Flying Start | FCE Grid | Unplanned
2020-10-13 14:24:00 | 2020-10-14 02:33:00 | 729 |  | LGS#1 Trip to standstill |  | Electrical | A1G1 CB | Hydro Total Blackout | External | Trip by 86 E Alarm | Flying Start | FCE Grid | Unplanned
2020-12-24 18:59:00 | 2020-12-24 19:39:00 | 40 |  | Total blackout |  | Electrical | A1L1 CB | Hydro Total Blackout | External | Trip to Standstill | Started to SNL | Auxiliary Grid | Unplanned
2019-02-02 17:52:00 | 2019-02-02 18:16:00 | 24 |  | LGS#1 Trip by lockout relay 86E |  | Electrical | Fire Deluge System | Unknown Reason | Internal | Trip by 86 E. 186T Alarm | - | FCE Grid | Unplanned
2019-04-21 01:15:00 | 2019-04-21 01:25:00 | 10 |  | LGS#1 Trip by 86N normal shutdown |  | Mechanical | Governor Oil | Low Pressure | Internal | Trip by 86N Alarm | Flying Start | FCE Grid | Unplanned
2019-04-25 06:07:00 | 2019-04-25 11:27:00 | 320 |  | LGS#1 Trip by 86E energized |  | Mechanical | Governor Turbine | Alarm Trip | Internal | Trip by 86E Alarm | Start | FCE Grid | Unplanned
2019-04-26 07:14:00 | 2019-04-26 07:19:00 | 5 |  | LGS#1 Trip by 86E energized |  |  | A1G1 CB | Breaker Trip | External | Trip by 86E Alarm | Flying Start | FCE Grid | Unplanned
2019-04-27 07:51:00 | 2019-04-27 08:11:00 | 20 |  | LGS#1 Trip by 86E energized |  | Electrical | A1G1 CB | Breaker Trip | External | Trip by 86 E Alarm | Flying Start | FCE Grid | Unplanned
2019-04-28 04:23:00 | 2019-04-28 04:35:00 | 12 |  | LGS#1 Trip by relay 86E & 86T tripped |  | Electrical | A1G1 CB | Breaker Trip | External | Trip by 86E, 86T Alarm | Flying Start | FCE Grid | Unplanned
2019-04-28 23:30:00 | 2019-04-28 23:33:00 | 3 |  | LGS#1 Trip by relay 86E & 86T tripped |  | Electrical | A1G1 CB | Breaker Trip | External | Trip by 86E, 86T Alarm | Flying Start | FCE Grid | Unplanned
2019-05-23 09:44:00 | 2019-05-23 11:45:00 | 121 |  | Total blackout |  | Electrical | A3L3 CB | Total Blackout | External | Trip | Flying Start | FCE Grid | Unplanned
2019-06-29 00:51:00 | 2019-06-29 12:06:00 | 675 |  | LGS#1 Trip due to relay 186T transformer lock out relay tripped |  | Electrical | A1G1 CB | Thermal Plant Shorted | External | Trip by 186T Alarm | Started via 4/CS | FCE Grid | Unplanned
2019-10-16 05:57:00 | 2019-10-16 06:31:00 | 34 |  | Total blackout |  | Electrical | A1L2 CB | Trip | External | Trip | Flying Start | FCE Grid | Unplanned
2019-12-14 19:14:00 | 2019-12-14 22:32:00 | 198 |  | LGS#1 Trip to standstill due to PLC error. |  | Instrument | A1G1 CB | PLC Major Fault | External | Trip to Standstill | Started via HMI | FCE Grid | Unplanned
2019-12-25 23:52:00 | 2019-12-26 00:16:00 | 24 |  | LGS#1 trip to srandstill by electrical overSpeed |  | Electrical | A1G1 CB | Thunder Strike | External | Trip to Standstill | Flying Start | FCE Grid